## SP-A20(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PFC-1WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 16 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PFC-1VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 500 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | STS304
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PFC-2WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ9×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ9×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PEC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-PEC-1WB-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | NYLON / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-FVC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A20-FVC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-A20(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-210
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-510
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-610
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-710
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-211
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-511
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-611
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A20-PFC-1WS-711
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 17 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-A40(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-1WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 12 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-1VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 500 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | STS304
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-2WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ4×Φ9×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ9×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PEC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PEC-1WB-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | NYLON / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-FVC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-FVC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 40~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-A40(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-210
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-510
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-610
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-710
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-211
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-511
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-611
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A40-PFC-1WS-711
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 35 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 40~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-A60(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PFC-3WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 8 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A40-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 1000 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | STS304
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A60-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-A60(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-210
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-510
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-610
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-710
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-211
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-511
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-611
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A60-PFC-3WS-711
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 60 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 8 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-A100(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-3WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 5 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 800 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | STS304
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A100-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.6 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-A100(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-210
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-510
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-610
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-710
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-211
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-511
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-611
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A100-PFC-3WS-711
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 110 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-A200(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-3WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 3 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 500 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | STS304
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | O-RING |  | FKM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PP
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PP
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | EPDM
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PP
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | EPDM
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PE / PVC
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.4 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.5 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | NONE
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-A200-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | METARIALS
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | HEAD |  | PVDF
17 | FEED NUMBER |  |  | SINGLE |  |  |  | DIAPHRAGM |  | PTFE
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | CHECK BALL |  | CERAMIC
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | BALL GUIDE |  | PVDF
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL SEAT |  | FKM(ETP)
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | JOINT |  | PVDF
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | O-RING |  | FKM(ETP)
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | SPRING(VALVE) |  | NONE
24 | CONTROLS | [6 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
25 | TYPE |  |  | MANUAL |  |  |  | DRIVE (SOLENOID)
26 | ADJUST. METHOD |  |  | STROKE LENGTH |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ADJUST. RANGE |  |  | 30~100% |  |  |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | RATED CURRENT |  | 0.5 |  |  | A
29 | ADJUST. RANGE |  |  | 1~100% |  |  |  | INSULATION CLASS |  | F
30 | WEIGHT |  |  | 2.6 |  |  | kg | PROTECTION CLASS |  | IP65
31 | COLOR | [6 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | POWER PLUG |  | EUROPE 16A 250V
34 | SPARE PAERTS | [6 empty] | ACCESSORIES
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | STRAINER FOOT V/V
37 | □ | SPRING(VALVE)
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-A200(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-210
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-510
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-610
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-710
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | NONE
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-211
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | □ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | □ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-511
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | □ | LEVEL S/W INPUT |  | □ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-611
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | □ | PULSE INPUT |  | □ | 1:1 |  |  | □ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-A200-PFC-3WS-711
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 150 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.25 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 100 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | METARIALS
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | HEAD |  | PP
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | DIAPHRAGM |  | PTFE
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | CHECK BALL |  | CERAMIC
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | BALL GUIDE |  | PP
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL SEAT |  | FKM
21 | CONTROLS | [9 empty] | JOINT |  | PP
22 | STROKE LENGTH |  |  | MANUAL | [6 empty] | O-RING |  | FKM
23 | ADJUSTMENT RANGE |  |  | 30~100% | [6 empty] | SPRING(VALVE) |  | NONE
24 | STROKE SPEED |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | HOSE (DIS./SUC.) |  | PE / PVC
25 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | DRIVE (SOLENOID)
26 | SIGNAL | [9 empty] | POWER CONSUMPTION |  | AVE 17 |  |  | W
27 | ■ | PULSE INPUT |  | □ | 1:1 |  |  | ■ | DIV/MUL |  | VOLTAGE |  | 1Φ AC220V 50/60Hz
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | RATED CURRENT |  | 0.5 |  |  | A
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | INSULATION CLASS |  | F
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | PROTECTION CLASS |  | IP65
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SIZE |  | 3C×0.75SQ×2m
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | POWER PLUG |  | EUROPE 16A 250V
34 | COLOR | [9 empty] | SPARE PAERTS
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
36 | ACCESSORIES | [9 empty] | □ | CHECK BALL |  | □ | O-RING
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | SPRING(VALVE)
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.